## Factory Option 1
DDRC-GRMS-E Factory Default Config | Dry Contact Inputs
| DC1 | DC2 | DC3 | DC4 | DC5 | DC6 | DC7 | DC8 | DC9 | DC10 | DC11 | DC12 | DC13 | DC14 | DC15 | DC16 | DC17 |  | DC18
| Bed side righ | Bed side left | Both Bed sides | Room lighting 1 | Room lighting 2 | Corridor lighting | Room & Corridor | Bath room lighting 1 | Bath room lighting 2 | Sheers open/close | Blind open/close | DND | MUR | Laundry Pick Up | Door Bell | Emergancy | Master lighting toggle ON/OFF |  | Card holder input ON/OFF
Channel 1 "Air Con" | [18 empty] | ON | OFF
Channel 2 "GPO" | [18 empty] | ON | OFF
Channel 3 "Bed side right" | [17 empty] | OFF |  | OFF | bar: DC1; DC3; DC16
Channel 4 "Bed side left" | [17 empty] | OFF |  | OFF | bar: DC2 to DC3; DC16
Channel 5 "Room lighting 1" | [17 empty] | OFF | ON | OFF | bar: DC4; DC7; DC16 to DC17
Channel 6 "Room lighting 2" | [17 empty] | OFF | ON | OFF | bar: DC5; DC7; DC16
Channel 7 "Corridor lighting" | [17 empty] | OFF | ON | OFF | bar: DC6 to DC7; DC16
Channel 8 "Bath lighting 1" | [17 empty] | OFF |  | OFF | bar: DC8; DC16 to DC17
Channel 9 "Bath lighting 2" | [17 empty] | OFF | ON | OFF | bar: DC9; DC16
Channel 10 Blind motor 1 power | [19 empty] | S5 | bar: DC10
Channel 11 Blind motor 1 direction | [19 empty] | S5 | bar: DC10
Channel 12 Blind motor 2 power | bar: DC11
Channel 13 Blind motor 2 direction | bar: DC11
Digital output 1 (DND) | bar: DC1 to DC12; DC16 to DC17
Digital output 2 (MUR) | bar: DC1 to DC11; DC13; DC16 to DC17
Digital output 3 (LPU) | bar: DC1 to DC11; DC14; DC16 to DC17
Digital output 4 (Door Bell) | bar: DC1 to DC11; DC15 to DC17
Area | A3 | A3 | A3 | A4 | A4 | A4 | A4 | A5 | A5 | A6 | A7 | A8 | A8 | A8 | A9 | A3-5 | A3-5 |  | A2-9
Logical Channel | 1 | 2 | All | 1 | 2 | 3 | All | 1 | 2 | 1 | 1 | 1 | 2 | 3 | 1
Tild mem ~ | ~1 | ~2 | ~3 | ~4 | ~5 | ~6 | ~7 | ~8 | ~9 | ~10 | ~11 | ~12 | ~13 | ~14 | ~15 | ~16 | ~17 |  | ~18
S1 & S2 Blind control input:
Long Press of DC10 would toggle the direction of the Sheers travel between open and close. Short closure of DC10 will stop the Sheers Travel.
Long Press of DC11 would toggle the direction of the Blinds travel between open and close. Short closure of DC11 will stop the Blinds Travel.
S3 - Door Bell:
Press of DC15 will pulse on for 1 second, delay of 1.5, and then pulse for 1 second. If the system is in DND mode then this function should be disabled.
S4 - Room status indicator:
‘Make Up Room’ is turned OFF and Button is Disabled when ‘Do Not Disturb’ is turned ON.
S5 - Card holder:
When the card is removed there will be a delay for switching off the lighting and closing the blinds.