## Instructions
How to use the BACnet point calculator Only fill in the orange cells in the License Calculartor tab. Leave greys cells unchanged. 1) For each BACnet point type required, enable the row in column D (1 = enabled, 0 = disabled) 2) Determine on which level the BACnet point is being reported to the BMS. The lower the level (project > floor > Area) the more points will be required. It is possible to report on multiple levels (e.g. project and floor level). Enable both rows in that case. 3) Once all rows are enabled the project specific parameters need to be filled in in the "Estimation" and "totals" sections. Note: The total number of areas and logical channels might not be known at this point. An estimate can be made based on estimated amount of areas (Cell I18) and the estimated average number of logical channels per area (Cell I6). Lamp & Driver points: Lamp and driver points are selected together but on BACnet side they are split. The license calculation is based on the combined point (so 1 point per driver) but if there is a cost per BACNet point to be integrated the extra points on BMS side needs to be taken into account. A change request is pending which will make it configurable to report the Lamp and driver issues on BACNet side together as well.

## License Calculator
No. | Function | Object type | Y=1/N=0 | BACnet Points (License count) | Actual BACnet points (towards BMS)
1 | Total Offline Devices | Job | 0 | 0 | 0 | Orange cells = Value to be configured
2 | Total Offline Devices | Floor | 0 | 0 | 0 | Grey cells = Do not change
3 | Total Driver and Lamps Faults | Job | 0 | 0 | 0 | Read the Instructions tab for more information
4 | Total Driver and Lamps Faults | Floor | 0 | 0 | 0
5 | Total Driver and Lamps Faults | Area | 1 | 220 | 440 | Estimation | Total
6 | Offline Device Alarm | Job | 0 | 0 | 0 | Channel/Area (average) | 3
7 | Offline Device Alarm | Floor | 0 | 0 | 0 | Safety margin | 20%
8 | Driver or Lamp Fault Alarm | Job | 0 | 0 | 0
9 | Driver or Lamp Fault Alarm | Floor | 0 | 0 | 0
10 | Driver or Lamp Fault Alarm | Area | 0 | 0 | 0 | Totals per project | Total
11 | System Manager Offline Device Alarm | SM | 0 | 0 | 0 | Job | 1
12 | System Manager Driver or Lamp Fault Alarm | SM | 0 | 0 | 0 | SM | 1
13 | Preset | Area | 0 | 0 | 0 | Floor | 5
14 | Current Temperature | Area | 0 | 0 | 0 | Device (+ Sensor, excl DALI devices) | 15
15 | Temperature Setpoint | Area | 0 | 0 | 0 | Dynet Sensors (for lux level) | 4
16 | Channel Level (estimate) | Channel | 0 | 0 | 0 | Driver | 100
17 | Driver Status | Driver | 0 | 0 | 0 | Areas | 220
18 | Lamp Status | Driver | 0 | 0 | 0 | Logical Channels (Areas timed channels per area) | 660
19 | Channel Runtime | Driver / physical channel | 0 | 0 | 0 | Physical Channels (outputs & DALI drivers) | 123
20 | Device Offline Status | Device | 1 | 15 | 15
21 | Light Level (lux) | Sensor | 1 | 15 | 15
TOTAL NUMBER OF POINTS |  | 250 |  |  | 470
TOTAL NUMBER OF POINTS (with margin) |  | 300 |  |  | 470
Recommended license |  | PDDEG-S BACnet 1k point licence

## Licenses
No order required | PDDEG-S BACnet 100 point licence | 100
SW913703370609 | PDDEG-S BACnet 1k point licence | 1000
SW913703370709 | PDDEG-S BACnet 5k Point licence | 5000
SW913703370809 | PDDEG-S BACnet 10k Point licence | 10000
Maximum limit reached

## Version
Item | Version
BACnet point calculator | 2.3
System Builder | 3.38
PDDEG-S firmware | 1.24